## Slide 1: MODULE IV SYSTEM CONTROLLER
Closed-Loop Controllers - Continuous and discrete process Controllers, Control Modes –Two –Step mode, Proportional Mode, Derivative Mode, Integral Mode, PID Controllers –Digital Controllers –Velocity Control –Adaptive Control

## Slide 2: INTRODUCTION
Need for closed loop control???
PROCESS AUTOMATION
Closed loop control???
controller – compares output to a required condition – converts error into control action – to reduce the error
How Error occurs???
Change due to external disturbance / change in set value
Category to control?????
Particular value
Event to occur or not
sequential – clock based / event based
control over a parameter

## Slide 3: CONT..
Modes???
How controller reacts to the error / how control action given for a error
Control modes???
  Two step mode
  Proportional mode
  Derivative mode
  Integral mode
  Combinations of mode – PD, PI, PID

## Slide 4: CONT…

## Slide 5: TERMINOLOGY
Lag – time taken to respond to change in condition
Steady state error – measure of accuracy of control system in tracking the set value input

## Slide 6: TWO-STEP METHOD

## Slide 7: PROPORTIONAL CONTROL MODE
Controller output α Error
Iout - Io= Kp . e
(Iout – Io) (s) = Kp . E(s)
Transfer function = KP

## Slide 8: CONT…
Proportional band
Controller output is fully closed to fully
open
Error 0% to 100%
(proportional band)
% change in controller output from
set point = Kp . % change in error
100% change in controller output = KP . Proportional band

## Slide 9: CONT…
KP is low large steady state error but stable response
KP is high small steady state error but unstable response

## Slide 10: DERIVATIVE CONTROL MODE
Controller output α Rate of change of Error
Iout – Io = KD . (de / dt)
(Iout – Io) (s) = KD s . E(s)
Transfer function = KD s
Do not respond to steady state error

## Slide 11: PROPORTIONAL PLUS DERIVATIVE CONTROL MODE
Controller output = Kp . e + KD . (de / dt)
Iout - Io= Kp . e + KD . (de / dt)
(Iout – Io) (s) = Kp . E(s) + KD s . E(s)
Transfer function = KP + KD s
= KD ( s + 1/TD)
TD = KP / KD
TD = derivative time constant

## Slide 12: INTEGRAL CONTROL MODE
Rate of change
of Controller output α Error
-
( - . E(s)
Transfer function = (1/s) KI
No response for sudden
Increase in error

## Slide 13: INTEGRAL PLUS PROPORTIONAL CONTROL MODE
Controller output = Kp . e +
Iout - Io= Kp . e +
(Iout – Io) (s) = Kp . E(s) + . E(s)
Transfer function = KP + (1/s) KI
= KP / s ( s + 1/TI)
TI = KP / KI
TI = integral time constant

## Slide 14: PID CONTROL MODE
Controller output = Kp . e +
Iout - Io= Kp . e + + KD . (de / dt)
(Iout – Io) (s) = Kp . E(s) + . E(s) + KD s . E(s)
Transfer function = KP + (1/s) KI + s KD
= KP ( 1 + + )

## Slide 15: CONT…
Proportional mode reduces steady-state errors, but always destabilize the system.
Integral control provides robust reduction in steady-state errors, but often makes the system less stable.
Derivative control improves stability, but has almost no effect on the steady state error

## Slide 16: CONT…